## Main Doc
Flow Chart Parts | Flow Chart Parts Name
D-1 | Profitability Page
D-2 | Electricity Unit Price Sheet
D-3 | Anodizing Production Plan Sheet
D-4 | Gas Unit Price Sheet

## PDI-PDO List
Parameter Alias | Parameter name | PDI/PDO | Tag Names | Description | Type | Meas unit
P1 | DG1 - Trigeneration Electricity Production | PDI | EnerMan_Gen1_Electricity_Generation_Counter_Value (kWh) |  | UDINT | kWh
P2 | DG2 - Trigeneration Electricity Production | PDI | EnerMan_Gen2_Electricity_Generation_Counter_Value (kWh) |  | UDINT | kWh
P3 | DG1 - Trigeneration Natural Gas Consumption | PDI | EnerMan_Gen1_Natural_Gas_Consumption_Counter_Value (m3) |  | UDINT | m3
P4 | DG2 - Trigeneration Natural Gas Consumption | PDI | EnerMan_Gen2_Natural_Gas_Consumption_Counter_Value (m3) |  | UDINT | m3
P5 | Domestic Electricity Consumption | PDI | TRIJEN TM - TRIJS-Q01.Ep |  | LREAL | kWh
P6 | DG1 - Hot Water Consumption | PDI | EnerMan_Gen1_Hot_Water_Consumption_Counter_Value (kWh) |  | UDINT | kWh
P7 | DG2 - Hot Water Consumption | PDI | EnerMan_Gen2_Hot_Water_Consumption_Counter_Value (kWh) |  | UDINT | kWh
P8 | DG1 - Hot Water Instantaneous Value | PDI | EnerMan_Gen1_Hot_Water_Consumption_Instantaneous_Value (kW) |  | REAL | kW
P9 | DG2 - Hot Water Instantaneous Value | PDI | EnerMan_Gen2_Hot_Water_Consumption_Instantaneous_Value (kW) |  | REAL | kW
P10 | Hot Water Outgoing Line-1 Temperature | PDI | EnerMan_Gen1_Hot_Water_Exit_Temperature (C) |  | REAL | ºC
P11 | Hot Water Return Line-1 Temperature | PDI | EnerMan_Gen1_Hot_Water_Return_Temperature (C) |  | REAL | ºC
P12 | Hot Water Outgoing Line-2 Temperature | PDI | EnerMan_Gen2_Hot_Water_Exit_Temperature (C) |  | REAL | ºC
P13 | Hot Water Return Line-2 Temperature | PDI | EnerMan_Gen2_Hot_Water_Return_Temperature (C) |  | REAL | ºC
P14 | DG1 - Steam Consumption | PDI | EnerMan_Gen1_Steam_Consumption_Counter_Value (kWh) | ABB is waiting for a solution. Flowmeter's Card will change with the new one. | UDINT | kWh
P15 | DG2 - Steam Consumption | PDI | EnerMan_Gen2_Steam_Consumption_Counter_Value (kWh) |  | UDINT | kWh
P16 | DG1 - Steam Instantaneous Value | PDI | EnerMan_Gen1_Steam_Consumption_Instantaneous_Value (kW) |  | REAL | kW
P17 | DG2 - Steam Instantaneous Value | PDI | EnerMan_Gen2_Steam_Consumption_Instantaneous_Value (kW) |  | REAL | kW
P18 | Lube Oil Consumption | PDI | EnerMan_Lube_Oil_Consumption_Counter_Value (m3) |  | LREAL | m3
P19 | Chemical Liquid Consumption | PDI | EnerMan_Chemical_Consumption_Counter_Value (m3) |  | LREAL | m3
P20 | Chemical Liquid Instantaneous Value | PDI | EnerMan_Chemical_Consumption_Instantaneous_Value (m3) |  | REAL | m3
P21 | Fresh Water Consumption | PDI | EnerMan_Fresh_Water_Consumption_Counter_Value (m3) |  | LREAL | m3
P22 | Fresh Water Instantaneous Value | PDI | EnerMan_Fresh_Water_Consumption_Instantaneous_Value (m3) |  | REAL | m3
P23 | Electricity unit price determined in the Energy Market | PDI | ???????? | Sent manually via Excel file | REAL | TL/MWh
P24 | System usage fee | PDI | ???????? | Last month's value | REAL | TL
P25 | Renewable energy tax | PDI | ???????? | Last month's value | REAL | TL
P26 | Unit price of natural gas used in trigeneration plant | PDI | ???????? | Last month's value | REAL | TL/Sm3
P27 | Trigeneration Operating Cost | PDI | ???????? | Sent manually via Excel file | REAL | TL/kWh
P28 | Unit price of natural gas used in the process | PDI | ???????? | Last month's value | REAL | TL/Sm3
P29 | Natural Gas Value Consumed per kW | PDI | ???????? | Sent manually via Excel file | INT | -
P30 | Spesific Natural Gas Consumption | PDO |  |  |  | Sm3/kWh
P31 | Spesific Lube Oil Consumption | PDO |  |  |  | lt/kWh
P32 | Spesific Fresh Water Consumption | PDO |  |  |  | lt/kWh
P33 | Process Electricity Unit Price | PDO |  |  |  | TL/kWh
P34 | Production Electricity Unit Price | PDO |  |  |  | TL/kWh
Note on F2: Sevasti Politi: 64bit

## Electricity Unit Price
Electricity unit price determined in the Energy Market (P23) |  |  | System usage fee (P24) | Renewable energy tax (P25) | Factory Electricity Consumption Value | Hourly Process Electricity Unit Price | Hourly Trigeneration Electricity Generation Unit Price | Natural Gas Value Consumed per kW (P29) | Trigeneration Natural Gas Unit Price (P26) | Trigeneration Operating Cost (P27)
Date | Time | Value(TL/MWh) | Last month's value (TL) | Last month's value (TL) | Last month's value (kWh) |  |  | 0.27 | Last month's value (TL/m3) | 0.185
2023-09-26 | 0:00 | 2199 | 2195112.22 | 115.802 | 13340665 | 2.4793 | 2.9568 |  | 10.2659
2023-09-26 | 1:00 | 1995.25 |  |  |  | 2.2756 | 2.9568
2023-09-26 | 2:00 | 1879.99 |  |  |  | 2.1603 | 2.9568
2023-09-26 | 3:00 | 1698.89 |  |  |  | 1.9792 | 2.9568
2023-09-26 | 4:00 | 1594.98 |  |  |  | 1.8753 | 2.9568
2023-09-26 | 5:00 | 1896.93 |  |  |  | 2.1773 | 2.9568
2023-09-26 | 6:00 | 1896.93 |  |  |  | 2.1773 | 2.9568
2023-09-26 | 7:00 | 1896.93 |  |  |  | 2.1773 | 2.9568
2023-09-26 | 8:00 | 2100.01 |  |  |  | 2.3804 | 2.9568
2023-09-26 | 9:00 | 2049 |  |  |  | 2.3293 | 2.9568
2023-09-26 | 10:00 | 1798.88 |  |  |  | 2.0792 | 2.9568
2023-09-26 | 11:00 | 1948.17 |  |  |  | 2.2285 | 2.9568
2023-09-26 | 12:00 | 1549.99 |  |  |  | 1.8303 | 2.9568
2023-09-26 | 13:00 | 1778.15 |  |  |  | 2.0585 | 2.9568
2023-09-26 | 14:00 | 1900 |  |  |  | 2.1803 | 2.9568
2023-09-26 | 15:00 | 2049 |  |  |  | 2.3293 | 2.9568
2023-09-26 | 16:00 | 2096.93 |  |  |  | 2.3773 | 2.9568
2023-09-26 | 17:00 | 2325 |  |  |  | 2.6053 | 2.9568
2023-09-26 | 18:00 | 2400 |  |  |  | 2.6803 | 2.9568
2023-09-26 | 19:00 | 2600 |  |  |  | 2.8803 | 2.9568
2023-09-26 | 20:00 | 2253.63 |  |  |  | 2.534 | 2.9568
2023-09-26 | 21:00 | 1745 |  |  |  | 2.0253 | 2.9568
2023-09-26 | 22:00 | 1748 |  |  |  | 2.0283 | 2.9568
2023-09-26 | 23:00 | 1594.97 |  |  |  | 1.8753 | 2.9568

## Anodizing Production Plan
Planned Production Date |  |  | 2023-09-27
10 Micron | 15 Micron | 20 Micron | 25 Micron | TOTAL
33000 | 6000 | - | - | 39000

## Gas Unit Price
Trigeneration Natural Gas Unit Price (P26) | Process Natural Gas Unit Price (P28) | Note: Since natural gas is not bought from the market, the value of the previous month will be referenced.
Last month's value (TL/m3) | Last month's value (TL/m3)
10.2659 | 9.6022

## Formulations
INPUTS |  |  | PDI-PDO ALIAS | Formula | OUTPUTS | Notes
D2 | a | Electricity unit price determined in the Energy Market | P23 | Explained with examples. | Process(Imported) electricity unit price
| b | System usage fee | P24
| c | Renewable energy tax | P25
D2 | a | Trigeneration Natural Gas Unit Price | P26 | Explained with examples. | Production Electricity Unit Price
| b | Trigeneration Operating Cost | P27
| c | Natural Gas Value Consumed per kW | P29
D1 | NOTE | Historical production data and electricity consumption data of the Anodizing Facility will be shared. You will be asked to find the coefficient value with these data. |  | c / (a x b) | Electricity Consumption Coefficient Note: The multiplication in the denominator should be done for all microns and summed. | Anodizing Hourly Production Data.xlsx (It is included in the email attachment) Sample calculation is on sheet 1.09.2023.
| a | Micron-based production data | Realized micron-based production values can be shared with excel.
| b | Product Base Energy Consumption Factor | in the table below
| c | Total anodized electricity consumption | OPC-UA or Excel

## PROFITABILITY PAGE
Constant Data |  |  |  |  | Planned production quantity | Calculated estimated electricity consumption | Trigeneration Natural Gas Unit Price (P26) | Process Natural Gas Unit Price (P28)
Electricity Production | Steam Amount |  | Hot Water Amount |  | kg | kWh | Last month's value (TL/m3) | Last month's value (TL/m3)
kW/h | kg/h | kcal/h | m3/h | kcal/h |  |  | 10.2659 | 9.6022
4000 | 2500 | 1460017 | 100 | 2009458
3500 | 2187.5 | 1277514.875 | 100 | 2009458 |  |  | Trigeneration Electricity Unit Price | Process Electricity Unit Price
3000 | 1875 | 1095012.75 | 100 | 2009458 |  |  | Last month's value (TL/kWh) | Last month's value (TL/kWh)
2500 | 1562.5 | 912510.625 | 100 | 2009458 |  |  | 2.96 | 2.632
Trigen Profitability Calculation Table with Example
| Electricity Production | Steam Amount | Hot Water Amount |  | Planned production quantity | Calculated estimated electricity consumption | Production and electricity data on 1.09.2023 were used. Normally forecast data will be used.
| kW/h | kcal | kcal |  | kg | kWh
| 3000 | 1095013 | 2009458 |  | 40118 | 40322
| Energy needed for 1 kg of product (steam, hot water, electricity) | [5 empty] | Note: Trigen profitability calculation can be made by considering that an anodizing boiler is working instead of trigen. Profitability will increase when the steam and hot water generated by electricity generation are used in trigen. If anodizing boilers operate instead of trigen, there will be separate costs for steam, hot water and electricity.
| Steam Amount |  | Hot Water Amount |  | Electricity Amount
| 655.0753 | kcal/kg | 1202.1285 | kcal/kg | 1.0051 | kWh/kg
| 0.079403 | m3/kg | 0.14571 | m3/kg
ANODIZING BOILER cost calculation in TL for 1kg of product | Steam | 0.76245 | These are the costs that will occur with the operation of the anodizing boiler. Note: Electricity cost calculation should be made based on hourly values in the energy market. What is done here is just an example.
| Hot Water | 1.3992
| Electricity | 2.6454
| Total cost(TL/kg) | 4.807
TRIGENERATION cost calculation in TL for 1kg of product | Electricity | 2.9751 | Note: Steam and Hot water are the normal result of electricity generation in a trigen plant. Naturally, no cost is reflected in these. We only reflect the electricity production cost.
| Total cost(TL/kg) | 2.9751
Note on C21: Abdullah Kaya: Amount of steam required to produce 1 kg of product (kcal)
Note on E21: Abdullah Kaya: Amount of hot water required to produce 1 kg of product (kcal)
Note on H21: Abdullah Kaya: Amount of electricity required to produce 1 kg of product
Note on C22: Abdullah Kaya: -We switched from kcal to m3 by dividing by 8250 -The amount of natural gas (m3) spent to obtain the steam needed for 1kg anodizing production
Note on E22: Abdullah Kaya: -We switched from kcal to m3 by dividing by 8250 -The amount of natural gas (m3) spent to obtain the hot water needed for 1kg anodizing production

## Anodizing Elec. Consp.
Date | Anodizing Electricity Consumption Value(kWh)
2023-09-01 | 40322
2023-09-02 | 32920
2023-09-03 | 3868
2023-09-04 | 42079
2023-09-05 | 38107
2023-09-06 | 41994
2023-09-07 | 37487
2023-09-08 | 38328
2023-09-09 | 40807
2023-09-10 | 3791
2023-09-11 | 43925
2023-09-12 | 39656
2023-09-13 | 40341
2023-09-14 | 40230
2023-09-15 | 42209
2023-09-16 | 39075
2023-09-17 | 8868
2023-09-18 | 43903
2023-09-19 | 41101
2023-09-20 | 44713
2023-09-21 | 44345
2023-09-22 | 40493
2023-09-23 | 40801
2023-09-24 | 8279
2023-09-25 | 51126